## Sheet1
Address | Variable | Belong to R/W | Data format | sign | Data Model
0000H 0001H | Current total energy | R | Each electric energy kWh occupy 4 byte XXXXXX.XX | unsigned | Dword
0002H 0003H | Reserved | Reserved | Reserved | unsigned | Dword
0004H 0005H | Reserved | Reserved | Reserved | unsigned | Dword
0006H 0007H | Reserved | Reserved | Reserved | unsigned | Dword
0008H 0009H | Current reversing energy | R | Each electric energy kWh occupy 4 byte XXXXXX.XX | unsigned | Dword
000AH 000BH | Current forword energy | R | Each electric energy kWh occupy 4 byte XXXXXX.XX | unsigned | Dword
000CH | Voltage | R | XXX.X V | unsigned | Word
000DH | Current | R | XX.XX A | unsigned | Word
000EH | Active power | R | XX.XXX KW | signed | Word
0010H | Power factor | R | X.XXX Kvar | unsigned | Word
0011H | Frequency | R | XX.XX | unsigned | Word
0012H | Reserved | Reserved | Reserved | unsigned | Word
0013H | Reserved | Reserved | Reserved | unsigned | Word
0014H | Reserved | Reserved | Reserved | unsigned | Word
0015H High Byte | Communication address | R/W | 001-247 | unsigned | Char
0015H Low byte | Communication baudrate | R/W | 01 —— 9600bps (default) 02 —— 4800bps 03 —— 2400bps 04 —— 1200bps | unsigned | Char